## CANDU2
CANDU 600 | PRIMARY HEAT TRANSPORT SYSTEM |  |  |  | by Bill Garland | Wm. J. Garland and B. Quon-Moll, "Engineering Applications of Current Microcomputer Software Packages",
OVERALL HEAT AND MASS BALANCE |  |  |  |  | based on the file | 11th Simulation Symposium on Reactor Dynamics and Plant Control,
OVERALL ERROR ANALYSIS |  |  |  |  | CANDU1.WKS | Royal Military College, Kingston, Ontario, 11 pages, April 22-24, l985.
see http://www.nuceng.ca/papers/conf.htm paper C11
| INPUT |  |  | OUTPUT
REFERENCE 100% FULL POWER
Ref_FP | 2064 | MW(TH) | QF= | 647.9941 | MW(TH)
FEEDWATER FLOW |  |  | eQF= | 4.4446 | MW(TH)
mf= | 836.51 | KG/S
emf= | 9.58 | KG/S | QR= | 81.6557 | MW(TH)
Nmf= | 4 |  | eQR= | 0.52363 | MW(TH)
hf= | 774.64 | KJ/KG
ehf= | 5.85 | KJ/KG | ms= | 913.34 | KG/S
Nhf= | 4 |  | ems= | 9.6213 | KG/S
REHEATER DRAINS FLOW
mr= | 76.83 | KG/S | STEAM POWER
emr= | 0.89 | KG/S | QS= | 2554 | MW(TH)
Nmr= | 4 |  | eQS= | 26.9288 | MW(TH)
hr= | 1062.81 | KJ/KG
ehr= | 5.85 | KJ/KG | SECONDARY SIDE POWER
Nhr= | 4
STEAM FLOW |  |  | QSS= | 1824.3502 | MW(TH)
hs= | 2796.33 | KJ/KG | eQSS= | 27.2982 | MW(TH)
ehs= | 1.26 | KJ/KG |  |  |  | Notes:
Nhs= | 4 | [5 empty] | On the primary side the following are measured:
Header temperatures -> infer enthalpies
REACTOR INLET HEADER |  |  | QCH = fission heat generated |  |  |  | On the secondary side the following are measured:
hrih= | 1100.63 | KJ/KG |  | 1821.3502 | MW(TH) |  |  | Feedwater flow and temperature -> infer enthalpy
REACTOR OUTLET HEADER |  |  | QHH = head to header power |  |  |  |  | Reheater drains flow and temperatue -> infer enthalpy
hroh= | 1308.1 | KJ/KG |  | 1810.3502 | MW(TH) |  |  | Steam flow and temperature -> infer enthalpy
QP= | 17 | MW(TH) | M = reactor D2O core flow |  |  |  | From the secondary side flows and enthalpies we calculate power.
QES = end shield heat loss |  |  |  | 8725.8411 | KG/S |  | From the power and primary side enthalpies we calculate primary flow.
| 2 | MW(TH) | THERMAL POWER GENERATED
QM = moderator heat loss |  |  |  | 1824.3502 | MW(TH) |  | Of course, errors propagate. We use Root Mean Squared (RMS) error propagation
| 3 | MW(TH) | % REACTOR FULL POWER |  |  |  | since the errors are independent.
QA = auxililiaries heat loss |  |  |  | 88.3891 | %
| 6 | MW(TH) | ERROR IN REACTOR POWER
QPL = piping heat loss |  |  |  | 27.2982 | MW(TH)
| 3 | MW(TH) | % ERROR IN REACTOR POWER
|  |  |  | 1.4963 | %
Reheater Drains
Feedwater
Steam
D2O out
D2O in
Steam Generator